SECTION 15172

VARIABLE FREQUENCY DRIVES

PART 1  GENERAL

1.01	SECTION INCLUDES

- Variable Frequency Drive (VFD).

1.02  	RELATED SECTIONS

- Section 16195 - Electrical Identification:  Engraved nameplates.

1.03  	REFERENCES

- NEMA ICS 3.1 - Safety Standards for Construction and Guide for Selection,

Installation and Operation of Variable Frequency Drive Systems.

- NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

- UL, and cUL Approved

- IEEE Standard 444 (ANSI-C343)

- IEEE Standard 519

- IEC:  146A

- UL 508C (Power Conversion)

- CSA 22.2 No. 14-95 (Industrial Control Equipment)

- UL 1995 (Plenum rating)

- EN 50178 (LVD)

- EN 61800-3

- IEC 529

- FCC CFR 47 Part 15 Subpart B

1.04  	SUBMITTALS

- Submit under provisions of Section 01340.

- Shop Drawings shall include:  Wiring diagrams, electrical schematics, front and side views of enclosures, overall dimensions, conduit entrance locations and requirements, nameplate legends, physical layout and enclosure details.

- Product Data:  Provide data sheets showing; voltage, ratings of customer use switching and over-current protective devices, short circuit ratings, and weights.

- Manufacturer's Installation Instructions and Technical Manuals:  Indicate application conditions and limitations of use stipulated by product testing agency specified under regulatory requirements.  Include instructions for storage, handling, protection, examination, preparation, installation, and starting of adjustable speed drive.  Document the sequence of operation, cautions and warnings, trouble shooting procedures, spare parts lists and programming guidance.

1.05	QUALITY ASSURANCE

- VFD shall have a minimum MTBF (mean time between failure) rating of 28 years (245,280 Hours).

1.06  	OPERATION AND MAINTENANCE DATA

- Submit under provisions of Section 01700.

- Include instructions for starting and operating VFD, and describe operating limits, which may result in hazardous or unsafe conditions.

1.07  	QUALIFICATIONS

- Manufacturer must have a minimum of 25 years of documented experience, 
specializing in variable frequency drives.

1.08  	DELIVERY, STORAGE, AND HANDLING

- Deliver, store, protect and handle products to site, under provisions of

Section 01610.

- Accept VFD on site in original packing.  Inspect for damage.

- Store in a clean, dry space.  Maintain factory wrapping, or provide an additional 
heavy canvas or heavy plastic cover, to protect units from dirt, water, construction debris, and traffic.

- Handle carefully, in accordance with manufacturer's written instructions, to avoid damage to components, enclosure, and finish.

1.09  	WARRANTY

- Provide VFD warranty, for one year from date of startup, not to exceed 18 months from date of shipment.  Warranty shall include parts, and labor allowance for repair hours.

PART 2  PRODUCTS

2.01  	MANUFACTURERS

- VFD shall be manufactured by Yaskawa Electric

- Drives and motors shall be by the same manufacturer.  Motors should be inverter duty rated, per NEMA MG1 parts 30 and 31, for motor-drive compatibility.

2.02  	DESCRIPTION

- Provide enclosed variable frequency drives suitable for operation at the current, 
voltage, and horsepower indicated on the schedule.  Conform to requirements of NEMA ICS 3.1.

2.03  	RATINGS

- VFD must operate, without fault or failure, when voltage varies plus 10% or minus 15% from rating, and frequency varies plus or minus 5% from rating.

- VFD shall be __________ volts, _______ Hz, 3 Phase

- Displacement Power Factor:  0.98 over entire range of operating speed and load.

- Operating Ambient Temperature:  -10 degrees C to 40 degrees C (14 degrees F to 104 degrees F)

- Humidity:  0% to 95% non-condensing.

- Altitude:  to 3,300 feet, higher altitudes achieved by derating.

- Minimum Efficiency:  96% at half speed; 98% at full speed.

- Starting Torque:  100% starting torque shall be available from 0.5 Hz. to 60 Hz.

- Overload capability:  110% of rated FLA (Full Load Amps) for 60 seconds; 180% of rated FLA, instantaneously.

- The VFD must meet the requirements for Radio Frequency Interference (RFI) above 7 MHz as specified by FCC regulations, part 15, subpart J, Class A devices.

- Total Harmonic Distortion (THD) compliance:

Given the information provided by the customer’s electric power single line diagram and distribution transformer data, the VFD manufacturer shall carry out an analysis of the system.  The analysis reviews the potential for the proposed equipment, and any existing equipment, to meet IEEE 519 (tables 10.2 and 10.3) recommendations at the Point of Common Coupling (PCC).  The result of the analysis shall determine if additional power quality improvement measures should be included in the proposal to meet the THD recommendations of IEEE 519.  The PCC shall be at the primary side of the main distribution transformer.

- VFDs must have a minimum short circuit rating of 65K amps RMS (100K amps RMS with a DC bus reactor) without additional input fusing.

2.04  	DESIGN

- VFD shall employ microprocessor based inverter logic, isolated from all power circuits.

- VFD shall include surface mount technology with protective coating.

- VFD shall employ a PWM (Pulse Width Modulated) power electronic system, consisting of:

- Input Section:

- VFD input power stage shall convert three-phase AC line power into a fixed DC voltage via a solid state full wave diode rectifier, with MOV (Metal Oxide Varistor) surge protection.

- Intermediate Section:

- DC bus as a supply to the VFD output Section shall maintain a 
fixed voltage with filtering and short circuit protection.

- DC bus shall be interfaced with the VFD diagnostic logic circuit, for continuous monitoring and protection of the power components.

- 30 HP to 150 HP @ 208 VAC, 30 HP to 150 HP @ 240 VAC, and 40 HP to 500 HP 480 VAC, VFDs shall include a DC bus reactor to minimize reflected harmonics.

- Output Section

- Insulated Gate Bipolar Transistors (IGBTs) shall convert DC bus voltage to variable frequency and voltage.

- The VFD shall employ PWM sine coded output technology to power the motor.

- The VFD must be selected for operation at carrier frequencies at or above 5 kHz 
without derating to satisfy the conditions for current, voltage, and horsepower as indicated on the equipment schedule.  Exception to this requirement is allowed only for VFDs providing 506 amps or more.

- VFD shall have an adjustable carrier frequency:  The carrier frequency shall have a minimum of six settings to allow adjustment in the field.

- VFD shall have embedded Building Automation System (BAS) protocols for network communications; Johnson Metasys N2, Siemens System 600 APOGEE, and Modbus/Memobus.  These protocols shall be accessible via a RS-422/485 communication port.

- VFD shall have a quick disconnect, removable control I/O terminal block to simplify control wiring procedures.

- VFD shall include two independent analog inputs.  One shall be 0-10 VDC.  The other shall be programmable for either 0-10 VDC or 4-20 mA.  Either input shall respond to a programmable bias and gain.

- VFD shall include a minimum of seven multi-function digital input terminals, capable of being programmed to determine the function on a change of state.  These terminals shall provide up to 30 functions, including, but not limited to:

- Remote/Local operation selection

- Detection of external fault condition

- Remote Reset

- Multi-step speed commands

- Run permissive

- Floating control

- VFD shall include two 0-10 VDC or 4-20 mA analog output for monitoring, or "speed tracking" the VFD.  The analog output signal will be proportional to output frequency, output current, output power, PI (Proportional & Integral control) feedback or DC bus voltage.

- VFD shall provide terminals for remote input contact closure, to allow starting in the automatic mode.

- VFD shall include at least one external fault input, which shall be programmable for a normally open or normally closed contact.  These terminals can be used for connection of firestats, freezestats, high pressure limits or similar safety devices.

- VFD shall include two form "A" contacts and one form "C" contact, capable of being programmed to determine conditions that must be met in order for them to change state.  These output relay contacts shall be rated for at least 5A at 120 VAC and shall provide up to 18 functions, including, but not limited to:

- Speed agree detection.

- Low and high frequency detection.

- Missing frequency reference detection.

- Overtorque/Undertorque detection

- Drive Running

- Drive Faulted

- VFD shall include a power loss ride through of 2 seconds.

- VFD shall have DC injection braking capability, to prevent fan “wind milling” at start or stop, adjustable, current limited.

- VFD shall have a motor preheat function to prevent moisture accumulation in an idle motor.

- VFD shall include diagnostic fault indication in selected language, last 10 faults storage and heatsink cooling fan operating hours.

- VFD shall have a digital operator with program copy and storage functions to simplify set up of multiple drives.  The digital operator shall be interchangeable for all drive ratings.

- VFD shall include a front mounted, sealed keypad operator, with an English 
language (or one of 6 additional international languages) illuminated LCD display.  The operator will provide complete programming, program copying, operating, monitoring, and diagnostic capability.  Keys provided shall include industry standard commands for Hand, Off, and Auto functions.

- VFD plain language display shall provide readouts of; output frequency in hertz, PI feedback in percent, output voltage in volts, output current in amps, output power in kilowatts, D.C. bus voltage in volts, interface terminal status, heatsink temperature and fault conditions.  All displays shall be viewed in an easy-to-read illuminated LCD with International language selectability.

- VFD unit shall include the following meters to estimate use of energy:

- Elapsed Time Meter

- Kilowatt Meter

- Kilowatt Hour Meter

- VFD shall include PI control logic, to provide closed loop setpoint control capability, from a feedback signal, eliminating the need for closed loop output signals from a building automation system.  The PI controller shall have a differential feedback capability for closed loop control of fans and pumps for pressure, flow or temperature regulation in response to dual feedback signals.

- An energy saving sleep function shall be available in both open loop (follower mode) and closed loop (PI) control, providing significant energy savings while minimizing operating hours on driven equipment.  When the sleep function senses a minimal deviation of a feedback signal from setpoint, or low demand in open loop control, the system reacts by stopping the driven equipment.  Upon receiving an increase in speed command signal deviation, the drive and equipment resume normal operation.

- VFD shall include loss of input signal protection, with a selectable response strategy including speed default to a percent of the most recent speed.

- VFD shall include electronic thermal overload protection for both the drive and motor.  The electronic thermal motor overload shall be approved by UL.  If the electronic thermal motor overload is not approved by UL, a separate UL approved thermal overload relay shall be provided in the VFD enclosure.

- VFD shall include the following program functions:

- Critical frequency rejection capability:  3 selectable, adjustable deadbands.

- Auto restart capability:  0 to 10 attempts with adjustable delay between attempts.

- Ability to close fault contact after the completion of all fault restart attempts.

- Stall prevention capability.

- "S" curve soft start capability.

- Bi-directional "Speed search" capability, in order to start a rotating load.

- 14 preset and 1 custom volts per hertz pattern.

- Heatsink over temperature speed fold back capability

- Terminal status indication.

- Program copy and storage in a removable digital operator.

- Current limit adjustment capability, from 30% to 200% of rated full load current of the VFD.

- Motor pre-heat capability

- Input signal or serial communication loss detection and response strategy.

- Anti "wind-milling" function capability.

- Automatic energy saving function.

- Undertorque/Overtorque Detection.

- Preset speeds

- VFD shall include factory settings for all parameters, and the capability for those settings to be reset.

- VFD shall include user parameter initialization capability to re-establish project specific parameters

- VFD shall include the capability to adjust the following functions, while the VFD is running:

- Speed command input.

- Acceleration adjustment from 0 to 6000 seconds.

- Deceleration adjustment from 0 to 6000 seconds.

- Select from 5 preset speeds.

- Analog monitor display.

- Removal of digital operator.

  - PRODUCT OPTIONS

Note to the Consulting Engineer; See Appendix One to Select Options to be Applied to a Specific Project

2.06  	FABRICATION

- All standard and optional features shall be included in a single NEMA 1, plenum rated enclosure with a UL certification label.

- 2.07  	SOURCE QUALITY CONTROL

- In-circuit testing of all printed circuit boards shall be conducted, to insure the proper mounting and correct value of all components.

- All printed circuit boards shall be burned in for 96 hours, at 85 degrees C.

- Final printed circuit board assemblies shall be functionally tested, via computerized test equipment.  All tests and acceptance criteria shall be preprogrammed.  All test results shall be stored as detailed quality assurance data.

- All fully assembled controls shall be functionally tested, with fully loaded induction motors.  The combined test data shall then be analyzed, to insure adherence to quality assurance specifications.

- Inspect and production test, under load, each completed VFD assembly.

PART 3  EXECUTION

3.01  	EXAMINATION

- Verify that surface is suitable for VFD installation.

- Do not install VFD until the building environment can be maintained, within the service conditions required by the manufacturer.

3.02  	INSTALLATION

- Install VFD where indicated, in accordance with manufacturer's written instructions and NEMA ICS 3.

- Tighten accessible connections and mechanical fasteners after placing VFD.

- Provide a nameplate label on each VFD, identifying rated horsepower, full load amperes, model number, service factor and voltage/phase rating.

3.03  	FIELD QUALITY CONTROL

- Field inspection and testing to be performed under provisions of Section 01400.

- Inspect completed installation for physical damage, proper alignment, anchorage, and grounding.

3.04  	MANUFACTURER'S FIELD SERVICES

- Prepare and start systems under provisions of Section 01400.

3.05		ADJUSTING

- Carry out adjusting work under provisions of Section 01700.  Make final adjustments to installed VFD, to assure proper operation of HVAC systems.

END OF SECTION

APPENDIX ONE

PRODUCT OPTIONS

Note to the Consulting Engineer; Select Options to be Applied to this Project, Insert in the Appropriate Specification Section

- Three Contactor Manual Bypass shall be provided when indicated by the schedule.  VFD and bypass components shall be mounted inside a common NEMA 1 enclosure, fully pre-wired, and ready for installation as a single UL listed device.  Bypass shall include the following:

- Input, output, and bypass contactors, to disconnect power to the VFD, when the motor is running in the bypass mode.

- 120 VAC control transformer, with fused primary.

- Magnetic overload relay, to protect the motor while operating in the bypass mode.

- Circuit breaker/disconnect switch, with a pad-lockable through-the-door handle mechanism.

- Control and safety circuit terminal strip.

- Drive/Bypass selector switch, Hand/Off/Auto selector switch, Normal/Test selector switch

- Switch selectable smoke purge, auto transfer to bypass and remote transfer functions.

- Pilot lights (22 mm LEDs) for "Control Power ", "Drive Fault", “Drive Run”, “Bypass Run”, “OL/Safety Fault” and “Smoke Purge”.

- Normal/Test selector switch, shall allow testing and adjustment of the VFD, while the motor is running in the bypass mode.

- Hand/Off/Auto selector switch shall provide the following operation:

- Hand Position - The drive is given a start command, operation is via the local speed input (digital operator or speed pot.).  If in bypass mode, the motor is running.

- Off Position - The start command is removed, all speed inputs are ignored, power is still applied to the drive.  If in bypass mode, the motor is stopped.

- Auto Position - The drive is enabled to receive a start command and speed input from a building automation system.  If in bypass mode, the motor start/stop is controlled by the building automation system

- Annunciation contacts for drive run, drive fault, bypass run and motor OL/safety fault.

- Damper control circuit with end of travel feedback capability.

- VFD operator/keypad selection, LCD or LED types.

- H/O/A control panel selection, Touch pad or rotary switch types.

- Two Contactor Manual Bypass shall be provided when indicated by the schedule.  VFD and bypass components shall be mounted inside a common NEMA 1 enclosure, fully pre-wired and ready for installation as a single UL listed device.  Bypass shall include the following:

- Drive output, and bypass contactors, to isolate the VFD from the motor, when the motor is running in the bypass mode.

- 120 VAC control transformer, with fused primary.

- Magnetic overload relay, to protect the motor while operating in the bypass mode.

- Disconnect switch, with a pad-lockable through-the-door handle mechanism.

- Control and safety circuit terminal strip.

- Door mounted control panel with; Drive/Bypass selector keys, Hand/Off/Auto selector keys, Normal/Test selector keys.

- Door mounted control panel with Pilot lights (LEDs) for “Control Power”, “Drive Ready”, “Drive Run”, “Drive Selected”,  “Drive Fault”, “Drivel Test”,  “Bypass Selected”,  “Bypass Run”, “Motor OL”, ”Safety Open” “Damper Closed”, “Auto Run”, Auto Transfer”, “Smoke Purge”, “Hand Mode”, “Off Mode”, and “Auto Mode”..

- Switch selectable Auto Transfer to bypass, Safety Interlock circuit and BAS Interlock circuit functions.

- Normal/Test selector keys, shall allow testing and adjustment of the VFD, while the motor is running in the bypass mode.

- Hand/Off/Auto selector keys shall provide the following operation:

- Hand Position - The drive is given a start command, operation is via the local speed input (digital operator/keypad).  If in bypass mode, the motor is running.

- Off Position - The start command is removed, all speed inputs are ignored, power is still applied to the drive.  If in bypass mode, the motor is stopped.

- Auto Position - The drive is enabled to receive a start command and speed input from a building automation system.  If in bypass mode, the motor start/stop is controlled by the building automation system

- Annunciation contacts; 3 Programmable Form C contacts (120 VAC, 5 Amp) for: “Motor Run”, “Damper Actuator”, “Auto Transfer”, “Drive Run”, “Hand Mode”, “Auto Mode”, “System Fault”, “Bypass Run” or ”Serial Com Run”.

- Damper control circuit with end of travel feedback capability.

- VFD operator/keypad selection, LCD or LED types.

- Soft start on transfer to bypass shall be provided.

- Enclosure:

- NEMA 1 extended enclosure, to house additional equipment within the VFD enclosure for VFDs not requiring Bypass.

- NEMA 12 FVFF (Forced Ventilation inlet Filter and outlet Filter) enclosures with filters and blower.

- NEMA 3R enclosures for outdoor installations.

- Oversized control transformer of ________VA shall be provided to power customer supplied logic circuits.

- RFI (Radio Frequency Interference) filters to further attenuate possible VFD generated noise shall be provided.

- Current limiting input fusing for short circuit protection of VFD semiconductor devices shall be provided.

- Pressure transducer (3 to 15 PSI input = 0 to 10 V DC output), to convert a pneumatic signal into an VFD Speed Command Input shall be provided.

- Line reactors shall be provided on the input side of the drive for harmonic suppression.

- Output reactors shall be provided on the output side of the drive for motor protection in long motor lead length situations.

- DC bus reactor, to attenuate harmonic distortion shall be provided on:  20 HP and below @ 208 VAC, 25 HP and below @ 240 VAC, and 30 HP and below @ 480 VAC.

- 12-Pulse phase shifting transformer shall be provided on:  25 HP to 150 HP @ 208 VAC, 30 HP to 150 HP @ 240 VAC, and 40 HP to 500 HP @ 480 VAC models to minimize THD generated by the VFD.

- 18-Pulse phase shifting transformer shall be provided on:  25 HP to 150 HP @ 208 VAC, 30 HP to 150 HP @ 240 VAC, and 40 HP to 500 HP @ 480 VAC models to minimize THD generated by the VFD.

- Analog output (4-20 mA), shall be provided to make available two analog current outputs.

- Multiple motor operation; Two motor “OR” control; Multiple motor “AND” control shall be provided.

- Two motor “OR” control allows local or remote motor operation selection between two individual motors (pump #1 “OR” auto “OR” pump #2).

- Multiple motor “AND” control allows the operation of several motors from one drive (pump #1, pump #2, “AND” pump # 3 are operated at the same speed via the output from one drive).

- Serial communication gateway for Echelon LonWorks shall be provided via an isolated RS-422/485 circuit board with the following features:

- Command and monitor in excess of 64 points.

- Ability to integrate into BYPASS configuration without losing end switch and/ or safety interlock functionality.

- Serial communication board self test.

- Drive parameter storage within communication board.

- Drive parameter download capability.

- Drive parameter comparison feature.

- 5 Indication LEDs to indicate power, reception, transmission, fault, and service of serial communications (Power, Rxd, Txd, Fault, Service).

- Polarity insensitive.

- Alternate network connection through RJ-45J plug/jack.

- Serial communication gateway for BACnet shall be provided via an isolated MS-TP RS-485 circuit board.

- Remote digital operator, with keypad and display, to control and monitor the VFD from a remote location shall be provided.

- Speed potentiometer shall be provided in addition to the digital keypad speed command capabilities.

- Output motor protection (dv/dt) filter shall be provided to accomplish, long motor lead length solutions.

- H/O/A selector switch shall be provided in addition to the digital keypad operation selection capabilities.

- Local/Remote selector switch shall be provided in addition to the digital keypad operation selection capabilities.

- Analog meter shall be provided in addition to the digital keypad monitoring capabilities.

- Relays, motor overload or time delay shall be provided.

- PC software and cable for parameter upload/download/graphing shall be provided.

- VFD Input MCP circuit breaker/disconnect shall be provided.

- VFD Input manual disconnect shall be provided.

- Engraved cabinet nameplates shall be provided.